| RedBin-N... | Fan belt monitoring via speed control switch up to 10.000 min-1 | RedBin - N |
| --- | --- | --- |
|  |  | RedBin - N - 2 |
|  |  | Subject to change! |

Electrical, explosion proof fan belt switch

24 VAC/DC supply voltage, output potential free switching contact

PTB-certified in acc. with ATEX directive 94/9/EC for zone 2, 22.

Compact. Easy installation. Universal. Cost effective. Safe.

| Type | Sensor | Supply | Range | Min. setting | Output switch | Max. ratings |
| --- | --- | --- | --- | --- | --- | --- |
| RedBin - N | Namur DIN19234 | 24 VAC/DC | 0.10,000 min-1 | 50 min-1 | pot. free contact | 250 VAC, 0.1A/30 V, 0.5 A |
| RedBin - N - 2 | as above, but with second switching output |  |  |  | 2 pot. free contacts | 250 VAC, 0.1A/30 V, 0.5 A |

| Application |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fan belt switch |  | Transducer with namur sensor |  | Installation kit 3 |  | Installation kit 4 |  |  |
|  |  |  |  | 2 mm Typ HWN |  | 2 mm |  |  |

| Description |  | Highlights |
| --- | --- | --- |
| The RedBin-N speed control switch generation up to 10,000 min-1 is a revolution for fan belt monitor transducers in HVAC systems, in chemical, pharmaceutical, industrial and Offshore-/Onshore plants, for use in hazardous areas zone 2 (gas) and zone 22 (dust). Highest protection class (ATEX) and IP 66 protection, small dimension, universal functions and technical data guarantee safe operation even under difficult environmental conditions. The switching points are scalable within the maxium ranges. The integrated display is for actual value indication which can be switched off. All sensors are programmable on site without any additional tools. RedBin-N-2 sensors are additionally equipped with a secondary switching output, which can be parameterized independently. |  | - For all type of gas, mixtures, vapours and dust for use in zone 2 and 22 No addionally Ex-i module required - No intrisically safe wiring/installation between panel and sensor required - No intrisically safe wiring/installation and no space in the panel required Integrated junction box - Powersupply24VAC/DC - Output potential free switching contact - Display with backlight, can be switched off - Scalable switching characteristics - Scalable starting bypass time Compact design and small dimension (L B H = 180 107 66 mm) - Robust aluminium housing in protection class IP 66 - Down to -20°C ambient temperature applicable - Password locking Optional second switching output |

| Technical data | RedBin-N… |
| --- | --- |
| Power supply | 24 VAC/DC ± 20% (19,2...28,8 VAC/DC) 50...60Hz |
| Current, power consumption | 150 mA, ~ 4 W, internal fuse 500 mAT, without bracket, not removable |
| Galvanic isolation | supply-output 1,5 kV |
| Electrical connection | terminals 0,14...2,5 mm2 at integrated junction box |
| Cable entry | 2 M16 1,5 Ex-e approved, cable diameter ~ Ø 5...10 mm |
| Protection class | Class I (grounded) |
| Display | LCD with backlight, display for configuration, user guidance, parameter and actual value indication via LEDs |
| Control elements | 3 buttons for configuration |
| Housing protection | IP66 in acc. to IEC 60529 |
| Housing material | aluminium casting, coated |
| Dimension / weight | L W H = 180 107 66 mm / ~ 950g |
| Amient temperature/-humidity | - 20...+ 50 °C / 0...95 % rH, non condensed |
| Storage temperature | - 20...+ 70°C |
| Measuring range | 0...10.000 min-1 |
| Range scalable on site | 50 min-1...10.000 min-1 |
| Maintenance | maintenance free, nevertheless maintenance must be complied with regional standards, rules and regulations |
| Sensor circuit | internal IS circuit |
| Sensor | Namur, DIN 19234 |
| Response time of sensor | T90 / 5 sec. |
| Accuracy of rotary speed | ± 0,5% of end value |
| Setting range hysteresis | 25 min-1 ...1000 min-1 (factory setting 50 min-1) |
| Start delay | 5 sec. |
| Mechanical life | 10 106 |
| Electrical life (rated load) | 100 103 |
| Wiring diagram (SB) | SB 1.0 / SB 2.0 |
| Installation sensor/tubing | in Ex-area zone 2, 22 |

| Explosion proof | RedBin-N... |  |
| --- | --- | --- |
| acc. to ATEX directive | PTB 2009 ATEX 2018 | 94/9/EC (ATEX) |
| Approval for gas | II3(1)G Ex nC[ia] IIC T6 | for zone 2 |
| Approval for dust | II3(1)D Ex tD A22 [iaD] IP66 T80°C | for zone 22 |
| CE-Mark | CE No. 0158 |  |
| EMC directive | RL 89/336/EC |  |
| Low voltage directive | RL 73/23/EC |  |
| Protection type | IP 66 in acc. to EN 60529 |  |
| Potential compensation | external PA-terminal, 4 mm2 |  |
| Protection Class | I (grounded) |  |
|  | overvoltage categorie II acc. to EN 61010-1 |  |

| Accessories |  |
| --- | --- |
| Installation kit 3 | Mounting set for Namur sensor onto ventilators up to 20.000 m3/h |
| Installation kit 4 | Mounting set for Namur sensor onto ventilators over 20.000 m3/h |
| MKR | Mounting bracket for round ducts up to Ø 600 mm |

Dimensions/Drillings

Electrical connection

RedBin-N... switches are equipped with a 24 VAC/DC power supply. The supply has to be connected at terminal 1 (-/~) and 2 (+/~). The electrical wiring must be realized via integrated junction box. If supply voltage 24 VAC/DC different from the relay voltage must be used different or double isolated cables. The starting bypass delay can be activated by a short circuit of terminal 2 and teminal 3 (AUB). An active bypass delay is indicated with green blinking LEDs. Attention: Do not open covers when circuits alive!

| Wiring Diagram RedBin-N / RedBin-N-S2 |  |
| --- | --- |
| RedBin-N... | SB 1.0 |
| function normal close (nc) or normal open (no) can be selected via menu SW-Ch2 (optional) SW-Ch1 SW-IN (GND) Relay output 250VAC 0,1A / 220VDC 0,1A 30 VAC/DC / 0,5 A If supply voltage 24 Vac/dc different from the relay voltage must be used different cables or double isolated. 24 VAC/DC PE AUB |  |

| Namur sensor connector | SB 2.0 |  |
| --- | --- | --- |
| Male connector blue (+) brown (-) namur sensor DIN 19234 | Values intrinsically safe (IS) for passive sensors |  |
|  | Uo = 9,6 V |  |
|  | Io = 9,7 mA |  |
|  | Po = 24 mW |  |
|  | Ci = 0 | Li = 0 |
|  | Co (IIC) = 840 nF |  |
|  | Lo (IIC) = 5 mH |  |

Display and Buttons

Display for programming and indication Push button ENTER Push button for level select

### Change operation-/parametrisation mode

To change from operation to parametrisation mode push the enter button  for minimum 3 seconds. Back over the menu save.

### Indication of data logging

The blinking unit in the display shows that datas received and the device is working.

Password input

The default / delievery setup is 0000. In this configuration the password input is not activated. To activate a password change the 4 digits into your choosen numbers (e.g 1234) and press Enter. Please keep your password in mind for next parameter change! Due to a new parameter setup the password is requested.

Installation

Relay output 250V 0,1A / 30 V / 0,5 A Supply 24V AC/DC +/- 20% safe area Ex area Zone 2, 22 Typ HWN 2,0 mm

- Do not open covers when circuits alive - The cable must be installed in a fixed position and protected against mechanical and thermical damage. - Connect protection earth - Avoid thermal transfer from sensor to transtucer (ensure max ambient temperature !) - Ambient temperature -20...+50 °C @ T6 - Close all covers, entries with min IP66 - All transducers are maintenance free. - Nevertheless maintenace must comply with regional standards, rules and regulations. - Close after settings all covers and cable entries tight min. IP66. - For outdoor installation a protective housing against rain, snow and sun should be applied - For electrical connection use the integrated junction box.

Important information for installation and operation

Installation, Commisioning, Maintenance The cable has to be drawn through the cable gland. After electrical connection the cable gland must be fixed tighten. IP66 must be fulfilled. In acc. with operation RedBin switches are maintenance free. Nevertheless maintenace must comply with regional standards, rules and regulations. The sensors must not be opened by the customer. For outdoor installation a protective housing against rain, snow and sun should be applied. For electrical connection use the internal junction box. Attention: Note the explosion proof rules before opening the internal junction box. Cut off the power supply. A. Supply and Contact Wires from safety extra low voltage must be separated from others. Only at 24 VAC/DC is supply and signal wires in one cable permitted. All others use separate or double isolated cables. Install overload protection fuse <10 A. B. Long cabeling For using long signal wires, shilded cables are recommended. The shield must be connected to the RedBin-P switch inside the terminal box. C. Separate ground wires Use for supply and signal wires a separate ground.